FIRE RISK ASSESSMENT.

SITE/LOCATION    Newry City Football ClubLtd.

ADDRESS.      .     The Showground’s Greenbank Newry

POST CODE BT34 2QX			TELEPHONE   028 3082 5648

AREA OF RISK ASSESMENT.	New Stand

DATE OF RISK ASSESMENT.	26th February 2008

COMPETENT PERSON(S):	W. J. SNEDDON M.I.F.P.O

SIGNED.

DATED.

This Fire Risk Assessment Has Been Carried Out To Satisfy

The Fire Precautions (Workplace) Regulations.

Northern (Ireland) 2001

The purpose of this report is to provide an assessment of the risk to life from fire in these premises, and        where appropriate, to make recommendations to ensure compliance with fire safety legislation. The                      report does not address the risk to property or business continuity from fire.

[GENERAL INFORMATION

| 1. | THE PREMISES |
| --- | --- |
| 1.1 | Number of floors: | Ground and First |
| 1.2 | Approximate floor area: | 40mt * 13 |
| 1.3 | Brief details of construction: |
|  | Stand built with block and concrete floor. Steel stanchions covered roof with cladding panels. |
| 1.4 | Occupancy |
|  | Sports Stand |
| 2. | THE OCCUPANTS |
| 2.1 | Approximate maximum number: | 560 |
| 2.2 | Approximate number of employees at any one time: | 10 |
| 2.3 | Maximum number of members of public: | 550 |
| 3. | OCCUPANTS AT SPECIAL RISK |
| 3.1 | Sleeping occupants: | 0 |
| 3.2 | Disabled occupants: | 4 |
| 3.3 | Occupants in remote areas: | 0 |
| 3.4 | Others: | 0 |
| 4. | FIRE LOSS EXPERIENCE NONE |

| 5. | OTHER RELEVANT INFORMATION |
| --- | --- |
|  | The following are contained under the seated area of the stand. Home and away changing rooms also shower areas. Referee’s area. Board room area. Toilet area for the public. There is an oil operated ram lift from the ground to first floor area. Press area enclosed with P V C cladding first floor area. On the outside wall of the stand there is an enclosed area approx 4mt *1mt which holds the main electrical switch gear for the ground. At the rear of the seated area on first floor there is a plant room which contains water tank, water cylinders, pumps and the equipment for the lift. To one side of the stand there is a block structure built which houses a stand by generator and boiler house. The generator at present has to be started manually but I have been assured by Mr A Williams that it is going to be converted to start automatically. I have also been informed that the generator will run all electrical equiptment within the ground. |

.

| 6. | RELEVANT FIRE SAFETY LEGISLATION |
| --- | --- |
| 6.1 | The Fire Precautions (Workplace) Regulations (Northern Ireland) 2001 apply to these | √ |
|  | Premises: |
| 6.2 | The Fire Services (Northern Ireland) Order 1984 applies to these premises, but a fire certificate is |
|  | Not required because the premises: |
|  | Have been exempted from a fire certificate by the fire authority. |  |
|  | Are put to a designated use, but a fire certificate is not required under the terms of the |  |
|  | Designation Order. |
| 6.3 | The Fire Services (Northern Ireland) Order 1984 applies to these premises, and a fire certificate is required by virtue of: |
|  | The number/location of guests and staff sleeping on the premises. |  |
|  | The number/location of persons employed at any one time. |  |
|  | The use of highly flammable or explosive materials. |  |
| 6.4 | A fire certificate has been issued under the Fire Services (Northern Ireland) Order 1984: |
|  | Certificate number: |  | Date of issue: |  |
| 6.5 | An application for a fire certificate was made on: |  |
|  | A notice specifying steps to be taken has not yet been issued by the fire authority: |  |
|  | A notice specifying steps to be taken was issued on: |  |
|  | And requires that work is completed by: |  |
| 6.6 | An application for a fire certificate should be made as soon as possible. |  |
| 6.7 | Other relevant fire safety legislation: |
|  | Safety of Sports Grounds ( Northern Ireland ) Order 2006 Management of Health and Safety at Work Regulations ( Northern Ireland ) 2000 |

| 6.8 | Comments: |
| --- | --- |
|  | In the case of buildings for which a fire certificate is in force, proposals to carry out material alterations must be notified to the fire authority. You are reminded that material alterations involving means of escape, fire warning systems or structural fire precautions, require approval from the building control authority. [This bullet point must appear as the last bullet point each time. If no other points, remove bullet point.] |

# FIRE HAZARDS AND THEIR ELIMINATION OR CONTROL

| 7. | ELECTRICAL SOURCES OF IGNITION |
| --- | --- |
| 7.1 | Reasonable measures taken to prevent fires of |
|  | Electrical origin? |  |  | Yes |  | No | √ |
| 7.2 | More specifically: |
|  | Fixed installation periodically inspected and tested? |  |  | Yes |  | No | √ |
|  | Portable appliance testing carried out? |  |  | Yes |  | No | √ |
|  | Suitable policy regarding the use of personal electrical |
|  | Appliances? |  |  | Yes |  | No | √ |
|  | Suitable limitation of trailing leads and adapters? |  |  | Yes | √ | No |  |
| 7.3 | Comments and hazards observed: No maintenance program in place |
|  | See Appendix |
| 8. | SMOKING |
| 8.1 | Reasonable measures taken to prevent fires as a result of |
|  | Smoking? |  |  | Yes | √ | No |  |
| 8.2 | More specifically: |
|  | Smoking prohibited in the building? |  |  | Yes | √ | No |  |
|  | Smoking prohibited in appropriate areas? |  |  | Yes | √ | No |  |
|  | Suitable arrangements for those who wish to smoke? |  |  | Yes | √ | No |  |
|  | Absence of any evidence of breaches of policy? |  |  | Yes | √ | No |  |
| 8.3 | Comments and hazards observed: |
|  | None |
| 9. | ARSON |
| 9.1 | Does basic security against arson by outsiders appear |
|  | Reasonable? |  |  | Yes | √ | No |  |
| 9.2 | Is there an absence of unnecessary fire load in close proximity to the premises or available for |
|  | Ignition by outsiders? |  |  | Yes | √ | No |  |
| 9.3 | Comments and hazards observed: |
|  | None |
| 10. | PORTABLE HEATERS AND HEATING INSTALLATIONS |
| 10.1 | Is the use of portable heaters avoided as far as practicable? |  |  | Yes | √ | No |  |
| 10.2 | If portable heaters are used, |
|  | Is the use of the more hazardous type (e.g. radiant bar |
|  | Fires or lpg appliances) avoided? | N/A | √ | Yes |  | No |  |
|  | Are suitable measures taken to minimize the hazard of |
|  | Ignition of combustible materials? | N/A |  | Yes | √ | No |  |
| 10.3 | Are fixed heating installations subject to regular |
|  | Maintenance? | N/A |  | Yes |  | No | √ |
| 10.4 | Comments and hazards observed: Maintenance program required for heating units See appendix |

| 11. | COOKING |
| --- | --- |
| 11.1 | Reasonable measures taken to prevent fires as a result of |
|  | Cooking? | N/A | √ | Yes |  | No |  |
| 11.2 | More specifically: |
|  | Filters changed and ductwork cleaned regularly? | N/A | √ | Yes |  | No |  |
|  | Suitable extinguishing appliances available? | N/A | √ | Yes |  | No |  |
| 11.3 | Comments and hazards observed: |
|  | None |
| 12. | LIGHTNING |
| 12.1 | Does the building have a lightning protection system? |  |  | Yes |  | No | √ |
| 12.2 | Comments and deficiencies observed: |
|  | See Appendix |
| 13. | OTHER SIGNIFICANT IGNITION SOURCES THAT WARRANT CONSIDERATION |
| 13.1 | Ignition sources: |
| 13.2 | Comments and hazards observed: |

| 14. | HOUSEKEEPING |
| --- | --- |
| 14.1 | Is the standard of housekeeping adequate? |  |  | Yes |  | No | √ |
| 14.2 | More specifically: |
|  | Combustible materials appear to be separated from |
|  | Ignition sources? |  |  | Yes | √ | No |  |
|  | Avoidance of unnecessary accumulation of combustible |
|  | Materials or waste? |  |  | Yes | √ | No |  |
|  | Appropriate storage of hazardous materials? | N/A | √ | Yes |  | No |  |
|  | Avoidance of inappropriate storage of combustible |  |  | Yes | √ | No |  |
|  | Materials? |
| 14.3 | Comments and hazards observed: |
|  | Most of the fire doors were held open by wedges. See Appendix |
| 15. | HAZARDS INTRODUCED BY OUTSIDE CONTRACTORS |
| 15.1 | Is there satisfactory control over works carried out in the |
|  | Building? |  |  | Yes |  | No | √ |
| 15.2 | Are fire safety conditions imposed on outside contractors? |  |  | Yes |  | No | √ |
|  | (Suitable guidance is contained in the following publications: Standard Fire Precautions for Contractors Engaged on Crown Works, Department of Environment, and HMSO. Fire Prevention on Construction Sites. Loss Prevention Council. Fire Safety in Construction Work. HSE. It is recommended that the guidance contained in these References be incorporated in contracts with outside Contractors.) |
| 15.3 | Comments: No issue of hot work permit in operation. |
|  | See Appendix |

# FIRE PROTECTION MEASURES

| 16. | MEANS OF ESCAPE |
| --- | --- |
| 16.1 | It is considered that the premises are provided with |
|  | Reasonable means of escape in case of fire. |  |  | Yes | √ | No |  |
| 16.2 | More specifically: |
|  | Adequate design of escape routes? |  |  | Yes | √ | No |  |
|  | Reasonable distances of travel? |  |  | Yes | √ | No |  |
|  | Suitable protection of escape routes? |  |  | Yes | √ | No |  |
|  | Adequate provision of exits? |  |  | Yes | √ | No |  |
|  | Suitable fire precautions for all inner rooms? | N/A |  | Yes | √ | No |  |
|  | Fire exits open in direction of escape where necessary? | N/A |  | Yes | √ | No |  |
|  | Exits easily and immediately openable where necessary? |  |  | Yes | √ | No |  |
|  | Avoidance of sliding or revolving doors as fire exits | N/A |  | Yes | √ | No |  |
|  | Where necessary? |
|  | Escape routes unobstructed? |  |  | Yes | √ | No |  |
| 16.3 | It is considered that the premises are provided with |
|  | Reasonable arrangements for means of escape for disabled |
|  | People. |  |  | Yes | √ | No |  |
| 16.4 | Comments and deficiencies observed: |
|  | None |
| 17. | MEASURES TO LIMIT FIRE SPREAD AND DEVELOPME |
| 17.1 | It is considered that there is: |
|  | Compartmentation of a reasonable standard. |  |  | Yes | √ | No |  |
|  | Reasonable limitation of linings that may promote fire |  |  | Yes | √ | No |  |
|  | Spread. |
| 17.2 | Comments and deficiencies observed: |
|  | None |
| 18. | ESCAPE LIGHTING |
| 18.1 | Reasonable standard of escape lighting system provided? |  |  | Yes |  | No | √ |
| 18.2 | Comments and deficiencies observed: |
|  | Escape Lighting should conform to that indicated in chapter 17.12 |
| 19. | FIRE SAFETY SIGNS AND NOTICES |
| 19.1 | Reasonable standard of fire safety signs and notices? |  |  | Yes | √ | No |  |
| 19.2 | Comments and deficiencies observed: |
|  | None |
| 20. | MEANS OF GIVING WARNING IN CASE OF FIRE |
| 20.1 | Reasonable manually operated electrical fire alarm system |
|  | Provided? |  |  | Yes | √ | No |  |
| 20.2 | Automatic fire detection provided? | Yes |  | Yes | √ | No |  |
|  | (Throughout Premises) | (Part of premises only) |  |  |  |
| 20.3 | Remote transmission of alarm signals? |  |  | Yes |  | No | √ |
| 20.4 | Comments and deficiencies observed? |
|  | The system was not operational on day of inspection |
|  | See Appendix |
| 21. | MANUAL FIRE EXTINGUISHING APPLIANCES |
| 21.1 | Reasonable provision of portable fire extinguishers? |  |  | Yes |  | No | √ |
| 21.2 | Hose reels provided? |  |  | Yes |  | No | √ |
| 21.3 | Comments and deficiencies observed: |
|  | 5kg Co2 should be placed in foyer for use on electrical switch gear at side of stand. See Appendix |
| 22. | RELEVANT‡ AUTOMATIC FIRE EXTINGUISHING SYSTEMS |
| 22.1 | Type of system: |
|  | None |
| 22.2 | Comments: |
| 23. | OTHER RELEVANT‡ FIXED SYSTEMS |
| 23.1 | Type of system: |
|  | None |
| 23.2 | Comments: |

# MANAGEMENT OF FIRE SAFETY

| 24. | PROCEDURES AND ARRANGEMENTS |
| --- | --- |
| 24.1 | Person responsible for fire safety: Yes |
|  | Mr A Williams |
| 24.2 | Competent person(s) available to assist in implementation of |
|  | Fire safety legislation? |  |  | Yes | √ | No |  |
|  | Mr R Mc Grath |
|  | Comments: |
|  | None |
| 24.3 | Appropriate fire procedures in place? |  |  | Yes | √ | No |  |
|  | Comments: |
| 24.4 | Persons nominated to respond to fire? | N/A |  | Yes |  | No | √ |
|  | Comments: See Appendix |
| 24.5 | Persons nominated to assist with evacuation? | N/A |  | Yes | √ | No |  |
|  | Comments: Ground Stewards |

| 24.6 | Appropriate liaison with fire brigade? | N/A |  | Yes | √ | No |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Comments: None |
| 24.7 | Routine in-house inspections of fire precautions (e.g. in the |
|  | Course of health and safety inspections)? | N/A |  | Yes | √ | No |  |
|  | Comments: Ground maintenance staff |
| 25. | TRAINING AND DRILLS |
| 25.1 | Is all staff given instruction on induction? |  |  | Yes |  | No | √ |
|  | Comments: See Appendix |
| 25.2 | Are all staff given periodic 'refresher training' at suitable |
|  | Intervals? |  |  | Yes |  | No | √ |
|  | Comments: See Appendix |
| 25.3 | Are staff with special responsibilities (e.g. fire wardens) given |
|  | Additional training? | N/A |  | Yes |  | No | √ |
|  | Comments: See Appendix |
| 25.4 | Are fire drills carried out at appropriate intervals? |  |  | Yes |  | No | √ |
|  | Comments See Appendix |
| 26. | TESTING AND MAINTENANCE |
| 26.1 | Adequate maintenance of workplace? |  |  | Yes | √ | No |  |
|  | Comments and deficiencies observed: None |
| 26.2 | Weekly testing and quarterly servicing of fire detection and |
|  | Alarm system? |  |  | Yes |  | No | √ |
|  | Comments and deficiencies observe |
|  | No contract with competent company. |
| 26.3 | Monthly, six-monthly and annual testing routines for |
|  | Emergency lighting? |  |  | Yes |  | No | √ |
|  | Comments and deficiencies observed: |
|  | No contract with competent company |
| 26.4 | Annual maintenance of fire extinguishing appliances? |  |  | Yes | √ | No |  |
|  | Comments and deficiencies observed: |
|  | No paper work at hand to verify above |
| 26.5 | Six-monthly inspection and annual testing of rising mains? | N/A | √ | Yes |  | No |  |
|  | Comments and deficiencies observed: |
|  | None |
| 26.6 | Weekly testing and periodic inspection of sprinkler |
|  | Installations? | N/A | √ | Yes |  | No |  |
|  | Comments: |
|  | None |

| 26.7 | Routine checks of final exit doors and/or security fastenings? | N/A |  | Yes | √ | No |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Comments: |
|  | Ground staff |
| 26.8 | Annual inspection and test of lightning protection system? | N/A |  | Yes |  | No | √ |
|  | Comments: |
|  | See Appendix |
| 26.9 | Other relevant inspections or tests: |
|  | Comments: |
| 27. | RECORDS |
| 27.1 | Appropriate records of: |
|  | Fire drills? | N/A |  | Yes |  | No | √ |
|  | Fire training? |  |  | Yes |  | No | √ |
|  | Fire alarm tests? | N/A |  | Yes |  | No | √ |
|  | Escape lighting tests? | N/A |  | Yes |  | No | √ |
|  | Maintenance and testing of other fire protection systems? | N/A |  | Yes |  | No | √ |
| 27.2 | Comments: |
|  | See Appendix |

# FIRE RISK ASSESSMENT

|  | The following simple risk level estimator is based on a more general health and safety risk level estimator contained in BS 8800: |
| --- | --- |

|  | Potential consequences of fire Fire hazard | Slightly harmful | Harmful | Extremely harmful |
| --- | --- | --- | --- | --- |
|  | Low | Trivial risk | Tolerable risk | Moderate risk |
|  | Medium | Tolerable risk | Moderate risk | Substantial risk |
|  | High | Moderate risk | Substantial risk | Intolerable risk |

|  | Taking into account the fire prevention measures observed at the time of this risk assessment, it is considered that the hazard from fire (probability of ignition) at these premises is: |
| --- | --- |
|  | Low |  | Medium | √ | High |  |
|  | Taking into account the nature of the premises and the occupants, as well as the fire protection and procedural arrangements observed at the time of this risk assessment, it is considered that the consequences for life safety in the event of fire would be: |
|  | Slightly harmful |  | Harmful | √ | Extremely harmful |  |
|  | In this context, our definition of the above terms is as follows: |
|  | Slightly harmful: | Outbreak of fire very unlikely to result in serious injury or death of any occupant. |
|  | Harmful: Extremely harmful | Outbreak of fire could result in harm to one or more occupants, but it is unlikely to result in serious injury or death of any occupant; any such injury or death is unlikely to involve multiples of people. Potential for serious injury or death of one or more occupants. |

|  | Accordingly, it is considered that the risk to life from fire at these premises is: |
| --- | --- |
|  | Trivial |  | Tolerable |  | Moderate | √ | Substantial |  | Intolerable |  |
|  | A suitable risk-based control plan should involve effort and urgency that is proportional to risk. The following risk-based control plan is based on one advocated by BS 8800 for general health and safety risks: |

| Risk Level | Action and timescale |
| --- | --- |
| Trivial | No action is required and no detailed records need be kept. |
| Tolerable | No major additional controls required. However, there may be a need for consideration of improvements that involve minor or limited cost. |
| Moderate | It is essential that efforts be made to reduce the risk. Risk reduction measures should be implemented within a defined time period. Where moderate risk is associated with extremely harmful consequences, further assessment may be required to establish more precisely the likelihood of harm as a basis for determining the priority for improved control measures. |
| Substantial | Considerable resources may have to be allocated to reduce the risk. If the building is unoccupied, it should not be occupied until the risk has been reduced. If the building is occupied, urgent action should be taken. |
| Intolerable | Building (or relevant area) should not be occupied until the risk is reduced. |

(Note that, although the purpose of this section is to place the fire risk in context, the above approach to risk assessment is subjective and for guidance only. All hazards and deficiencies identified in this report should be addressed by implementing all recommendations contained in the following section. The risk assessment should be repeated periodically.)

# Footnotes

Note:  If specific advice on security (including security again arson) is required, the advice of a security specialist should be obtained.

Based on visual inspection of readily accessible areas, with a degree of sampling where appropriate.

Based on visual inspection, but no test of illuminance levels or verification of full compliance with relevant British Standard carried out.

Based on visual inspection, but no audibility tests or verification of full compliance with relevant British Standard carried out.

‡ Relevant to life safety and this risk assessment (as opposed to property protection).

This is not intended to represent a legal interpretation of responsibility, but merely reflects the managerial arrangement in place at the time of this risk assessment.

BS 8800: 1996.  Guide to occupational health and safety management systems.